## RO Registers
Table | No. | Address | Bytes | Function Description | R/W | Type | Unit | Accuracy | Note | manual definition | length | poller start
1.2.1 | 1 | 10000 | 8 | Device SN | RO | STR | N/A | 1 | Read bytes to string | 1 |  | Bridge poller ro 10000 [ start="10000, length=
1.2.1 | 1 | 10001 | [7 empty] | 1
1.2.1 | 1 | 10002 | [7 empty] | 1
1.2.1 | 1 | 10003 | [7 empty] | 1
1.2.1 | 1 | 10004 | [7 empty] | 1
1.2.1 | 1 | 10005 | [7 empty] | 1
1.2.1 | 1 | 10006 | [7 empty] | 1
1.2.1 | 1 | 10007 | [7 empty] | 1
1.2.1 | 2 | 10008 | 1 | Inverter Model | RO | U16 | N/A | 1 | Please refer to table 3.2 | 1
1.2.1 | 3 | 10011 | 2 | Firmware Version | RO | U32 | N/A | 1 | Read bytes | 1
1.2.1 | 3 | 10012 | [7 empty] | 1
1.2.1 | 4 | 10100 | 1 | Date: Y/M | RO | U16 | N/A | 1 | Continuous read | 1
1.2.1 | 5 | 10101 | 1 | Time: D/H | RO | U16 | N/A | 1 |  | 1
1.2.1 | 6 | 10102 | 1 | Time: M/S | RO | U16 | N/A | 1 |  | 1
1.2.1 | 7 | 10104 | 1 | Safety Code | RO | U16 | N/A | 1 |  | 1
1.2.1 | 8 | 10105 | 1 | Inverter Working Status | RO | U16 | N/A | 1 | 0: Wait for grid connection 1: Self-checking 2: On-grid generating 3: Device fault 4: Firmware upgrade 5: Off-grid generating
1.2.1 | 9 | 10112 | 2 | Fault FLAG1 | RO | U32 | N/A | 1 | Please refer to table 3.3 | 1
1.2.1 | 9 | 10113 | [7 empty] | 1
1.2.1 | 10 | 10114 | 2 | Fault FLAG2 | RO | U32 | N/A | 1 |  | 1
1.2.1 | 10 | 10115 | [7 empty] | 1
1.2.1 | 11 | 10120 | 2 | Fault FLAG3 | RO | U32 | N/A | 1 |  | 1
1.2.1 | 11 | 10121 | [7 empty] | 1
1.2.1 | 12 | 10994 | 2 | Pmeter on phase A | RO | I32 | kW | 1000 |  |  |  |  | Thing data do012 "Pmeter on phase A" [ readValue="int32", readStart=10994 ] // unit="kW " | // unit="kW "
1.2.1 | 12 | 10995
1.2.1 | 13 | 10996 | 2 | Pmeter on phase B | RO | I32 | kW | 1000 |  |  |  |  | Thing data do013 "Pmeter on phase B" [ readValue="int32", readStart=10996 ] // unit="kW " | // unit="kW "
1.2.1 | 13 | 10997
1.2.1 | 14 | 10998 | 2 | Pmeter on phase C | RO | I32 | kW | 1000 |  |  |  |  | Thing data do014 "Pmeter on phase C" [ readValue="int32", readStart=10998 ] // unit="kW " | // unit="kW "
1.2.1 | 14 | 10999
1.2.1 | 15 | 11000 | 2 | Pmeter of three phases | RO | I32 | kW | 1000 |  |  |  |  | Thing data do015 "Pmeter of three phases " [ readValue="int32", readStart=11000 ] // unit="kW " | // unit="kW "
1.2.1 | 15 | 11001
1.2.1 | 16 | 11002 | 2 | Total Grid-Injection Energy on Meter | RO | U32 | kWh | 100 |  |  |  |  | Thing data do016 "Total Grid-Injection Energy on Meter" [ readValue="uint32", readStart=11002 ] // unit="kWh " | // unit="kWh "
1.2.1 | 16 | 11003
1.2.1 | 17 | 11004 | 2 | Total Purchasing Energy from Grid on Meter | RO | U32 | kWh | 100 |  |  |  |  | Thing data do017 "Total Purchasing Energy from Grid on Meter " [ readValue="uint32", readStart=11004 ] // unit="kWh " | // unit="kWh "
1.2.1 | 17 | 11005
1.2.1 | 18 | 11006 | 1 | AB line voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do018 "AB line voltage " [ readValue="uint16", readStart=11006 ] // unit="V " | // unit="V "
1.2.1 | 19 | 11007 | 1 | BC line voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do019 "BC line voltage " [ readValue="uint16", readStart=11007 ] // unit="V " | // unit="V "
1.2.1 | 20 | 11008 | 1 | CA line voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do020 "CA line voltage " [ readValue="uint16", readStart=11008 ] // unit="V " | // unit="V "
1.2.1 | 21 | 11009 | 1 | Phase A Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do021 "Phase A Voltage " [ readValue="uint16", readStart=11009 ] // unit="V " | // unit="V "
1.2.1 | 22 | 11010 | 1 | Phase A Current | RO | U16 | A | 10 |  |  |  |  | Thing data do022 "Phase A Current " [ readValue="uint16", readStart=11010 ] // unit="A " | // unit="A "
1.2.1 | 23 | 11011 | 1 | Phase B Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do023 "Phase B Voltage " [ readValue="uint16", readStart=11011 ] // unit="V " | // unit="V "
1.2.1 | 24 | 11012 | 1 | Phase B Current | RO | U16 | A | 10 |  |  |  |  | Thing data do024 "Phase B Current " [ readValue="uint16", readStart=11012 ] // unit="A " | // unit="A "
1.2.1 | 25 | 11013 | 1 | Phase C Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do025 "Phase C Voltage " [ readValue="uint16", readStart=11013 ] // unit="V " | // unit="V "
1.2.1 | 26 | 11014 | 1 | Phase C Current | RO | U16 | A | 10 |  |  |  |  | Thing data do026 "Phase C Current " [ readValue="uint16", readStart=11014 ] // unit="A " | // unit="A "
1.2.1 | 27 | 11015 | 1 | Grid Frequency | RO | U16 | Hz | 100 |  |  |  |  | Thing data do027 "Grid Frequency " [ readValue="uint16", readStart=11015 ] // unit="Hz " | // unit="Hz "
1.2.1 | 28 | 11016 | 2 | P_AC | RO | I32 | kW | 1000 |  |  |  |  | Thing data do028 "P_AC " [ readValue="int32", readStart=11016 ] // unit="kW " | // unit="kW "
1.2.1 | 28 | 11017
1.2.1 | 29 | 11018 | 2 | Energy-today | RO | U32 | kWh | 10 |  |  |  |  | Thing data do029 "Energy-today " [ readValue="uint32", readStart=11018 ] // unit="kWh " | // unit="kWh "
1.2.1 | 29 | 11019
1.2.1 | 30 | 11020 | 2 | Energy-total | RO | U32 | kWh | 10 |  |  |  |  | Thing data do030 "Energy-total " [ readValue="uint32", readStart=11020 ] // unit="kWh " | // unit="kWh "
1.2.1 | 30 | 11021
1.2.1 | 31 | 11022 | 2 | Total Generation Hours | RO | U32 | H | 1 |  |  |  |  | Thing data do031 "Total Generation Hours" [ readValue="uint32", readStart=11022 ] // unit="H " | // unit="H "
1.2.1 | 31 | 11023
1.2.1 | 32 | 11028 | 2 | Total PV Input Power | RO | U32 | kW | 1000 |  |  |  |  | Thing data do032 "Total PV Input Power" [ readValue="uint32", readStart=11028 ] // unit="kW " | // unit="kW "
1.2.1 | 32 | 11029
1.2.1 | 33 | 11032 | 1 | Temp.1 | RO | I16 | °C | 10 |  |  |  |  | Thing data do033 "Temp.1 " [ readValue="int16", readStart=11032 ] // unit="°C" | // unit="°C"
1.2.1 | 34 | 11033 | 1 | Temp.2 | RO | I16 | °C | 10 |  |  |  |  | Thing data do034 "Temp.2 " [ readValue="int16", readStart=11033 ] // unit="°C" | // unit="°C"
1.2.1 | 35 | 11034 | 1 | Temp.3 | RO | I16 | °C | 10 |  |  |  |  | Thing data do035 "Temp.3 " [ readValue="int16", readStart=11034 ] // unit="°C" | // unit="°C"
1.2.1 | 36 | 11035 | 1 | Temp.4 | RO | I16 | °C | 10 |  |  |  |  | Thing data do036 "Temp.4 " [ readValue="int16", readStart=11035 ] // unit="°C" | // unit="°C"
1.2.1 | 37 | 11038 | 1 | PV1 Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do037 "PV1 Voltage " [ readValue="uint16", readStart=11038 ] // unit="V " | // unit="V "
1.2.1 | 38 | 11039 | 1 | PV1 Current | RO | U16 | A | 10 |  |  |  |  | Thing data do038 "PV1 Current " [ readValue="uint16", readStart=11039 ] // unit="A " | // unit="A "
1.2.1 | 39 | 11040 | 1 | PV2 Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do039 "PV2 Voltage " [ readValue="uint16", readStart=11040 ] // unit="V " | // unit="V "
1.2.1 | 40 | 11041 | 1 | PV2 Current | RO | U16 | A | 10 |  |  |  |  | Thing data do040 "PV2 Current " [ readValue="uint16", readStart=11041 ] // unit="A " | // unit="A "
1.2.1 | 41 | 11062 | 2 | PV1 Input Power | RO | U32 | kW | 1000 |  |  |  |  | Thing data do041 "PV1 Input Power " [ readValue="uint32", readStart=11062 ] // unit="kW " | // unit="kW "
1.2.1 | 41 | 11063
1.2.1 | 42 | 11064 | 2 | PV2 Input Power | RO | U32 | kW | 1000 |  |  |  |  | Thing data do042 "PV2 Input Power " [ readValue="uint32", readStart=11064 ] // unit="kW " | // unit="kW "
1.2.1 | 42 | 11065
1.2.1 | 43 | 18000 | 2 | ARM Fault FLAG1 | RO | U32 | N/A | 1 | Please refer to table 3.3 | 1
1.2.1 | 43 | 18001 | [7 empty] | 1
1.2.1 | 44 | 30200 | 1 | Backup_A_V | RO | U16 | V | 10 | AC Voltage |  |  |  | Thing data do044 "Backup_A_V " [ readValue="uint16", readStart=30200 ] // unit="V " | // unit="V "
1.2.1 | 45 | 30201 | 1 | Backup_A_I | RO | U16 | A | 10 | AC Current |  |  |  | Thing data do045 "Backup_A_I " [ readValue="uint16", readStart=30201 ] // unit="A " | // unit="A "
1.2.1 | 46 | 30202 | 1 | Backup_A_F | RO | U16 | Hz | 100 | Frequency |  |  |  | Thing data do046 "Backup_A_F " [ readValue="uint16", readStart=30202 ] // unit="Hz " | // unit="Hz "
1.2.1 | 47 | 30204 | 2 | Backup_A_P | RO | I32 | kW | 1000 | AC Active Power |  |  |  | Thing data do047 "Backup_A_P " [ readValue="int32", readStart=30204 ] // unit="kW " | // unit="kW "
1.2.1 | 47 | 30205
1.2.1 | 48 | 30210 | 1 | Backup_B_V | RO | U16 | V | 10 | AC Voltage |  |  |  | Thing data do048 "Backup_B_V " [ readValue="uint16", readStart=30210 ] // unit="V " | // unit="V "
1.2.1 | 49 | 30211 | 1 | Backup_B_I | RO | U16 | A | 10 | AC Current |  |  |  | Thing data do049 "Backup_B_I " [ readValue="uint16", readStart=30211 ] // unit="A " | // unit="A "
1.2.1 | 50 | 30212 | 1 | Backup_B_F | RO | U16 | Hz | 100 | Frequency |  |  |  | Thing data do050 "Backup_B_F " [ readValue="uint16", readStart=30212 ] // unit="Hz " | // unit="Hz "
1.2.1 | 51 | 30214 | 2 | Backup_B_P | RO | I32 | kW | 1000 | AC Active Power |  |  |  | Thing data do051 "Backup_B_P " [ readValue="int32", readStart=30214 ] // unit="kW " | // unit="kW "
1.2.1 | 51 | 30215
1.2.1 | 52 | 30220 | 1 | Backup_C_V | RO | U16 | V | 10 | AC Voltage |  |  |  | Thing data do052 "Backup_C_V " [ readValue="uint16", readStart=30220 ] // unit="V " | // unit="V "
1.2.1 | 53 | 30221 | 1 | Backup_C_I | RO | U16 | A | 10 | AC Current |  |  |  | Thing data do053 "Backup_C_I " [ readValue="uint16", readStart=30221 ] // unit="A " | // unit="A "
1.2.1 | 54 | 30222 | 1 | Backup_C_F | RO | U16 | Hz | 100 | Frequency |  |  |  | Thing data do054 "Backup_C_F " [ readValue="uint16", readStart=30222 ] // unit="Hz " | // unit="Hz "
1.2.1 | 55 | 30224 | 2 | Backup_C_P | RO | I32 | kW | 1000 | AC Active Power |  |  |  | Thing data do055 "Backup_C_P " [ readValue="int32", readStart=30224 ] // unit="kW " | // unit="kW "
1.2.1 | 55 | 30225
1.2.1 | 56 | 30230 | 2 | Total_Backup_P | RO | I32 | kW | 1000 | Total Active Power |  |  |  | Thing data do056 "Total_Backup_P " [ readValue="int32", readStart=30230 ] // unit="kW " | // unit="kW "
1.2.1 | 56 | 20231
1.2.1 | 57 | 30236 | 2 | Invt_A_P | RO | I32 | kW | 1000 | Phase A Active Power |  |  |  | Thing data do057 "Invt_A_P " [ readValue="int32", readStart=30236 ] // unit="kW " | // unit="kW "
1.2.1 | 57 | 30237
1.2.1 | 58 | 30242 | 2 | Invt_B_P | RO | I32 | kW | 1000 | Phase B Active Power |  |  |  | Thing data do058 "Invt_B_P " [ readValue="int32", readStart=30242 ] // unit="kW " | // unit="kW "
1.2.1 | 58 | 30243
1.2.1 | 59 | 30248 | 2 | Invt_C_P | RO | I32 | kW | 1000 | Phase C Active Power |  |  |  | Thing data do059 "Invt_C_P " [ readValue="int32", readStart=30248 ] // unit="kW " | // unit="kW "
1.2.1 | 59 | 30249
1.2.1 | 60 | 30254 | 1 | Battery_V | RO | U16 | V | 10 | Battery Voltage |  |  |  | Thing data do060 "Battery_V " [ readValue="uint16", readStart=30254 ] // unit="V "
1.2.1 | 61 | 30255 | 1 | Battery_I | RO | I16 | A | 10 | Battery Voltage |  |  |  | Thing data do061 "Battery_I " [ readValue="int16", readStart=30255 ] // unit="A "
1.2.1 | 62 | 30256 | 1 | Battery_Mode | RO | U16 | N/A | 1 | 0: discharge 1: charge |  |  |  | Thing data do062 "Battery_Mode " [ readValue="uint16", readStart=30256 ] // unit="N/A "
1.2.1 | 63 | 30258 | 2 | Battery_P | RO | I32 | kW | 1000 | Battery Power |  |  |  | Thing data do063 "Battery_P " [ readValue="int32", readStart=30258 ] // unit="kW "
1.2.1 | 63 | 30259
1.2.1 | 64 | 31000 | 1 | Daily Energy Injected to Grid | RO | U16 | kWh | 10 |  |  |  |  | Thing data do064 "Daily Energy Injected to Grid" [ readValue="uint16", readStart=31000 ] // unit="kWh "
1.2.1 | 65 | 31001 | 1 | Daily Purchased Energy | RO | U16 | kWh | 10 |  |  |  |  | Thing data do065 "Daily Purchased Energy" [ readValue="uint16", readStart=31001 ] // unit="kWh "
1.2.1 | 66 | 31002 | 1 | Daily Energy Output on Backup | RO | U16 | kWh | 10 |  |  |  |  | Thing data do066 "Daily Energy Output on Backup" [ readValue="uint16", readStart=31002 ] // unit="kWh "
1.2.1 | 67 | 31003 | 1 | Daily Battery Charging Energy | RO | U16 | kWh | 10 |  |  |  |  | Thing data do067 "Daily Battery Charging Energy" [ readValue="uint16", readStart=31003 ] // unit="kWh "
1.2.1 | 68 | 31004 | 1 | Daily Battery Discharging | RO | U16 | kWh | 10 |  |  |  |  | Thing data do068 "Daily Battery Discharging" [ readValue="uint16", readStart=31004 ] // unit="kWh "
1.2.1 | 69 | 31005 | 1 | Daily PV Generation | RO | U16 | kWh | 10 |  |  |  |  | Thing data do069 "Daily PV Generation" [ readValue="uint16", readStart=31005 ] // unit="kWh "
1.2.1 | 70 | 31006 | 1 | Daily Load Consumption | RO | U16 | kWh | 10 |  |  |  |  | Thing data do070 "Daily Load Consumption" [ readValue="uint16", readStart=31006 ] // unit="kWh "
1.2.1 | 71 | 31008 | 1 | Daily Energy Purchased from Grid at Inverter | RO | U16 | kWh | 10 |  |  |  |  | Thing data do071 "Daily Energy Purchased from Grid at Inverter" [ readValue="uint16", readStart=31008 ] // unit="kWh "
1.2.1 | 72 | 31102 | 2 | Total Energy Injected into Grid | RO | U32 | kWh | 10 |  |  |  |  | Thing data do072 "Total Energy Injected into Grid" [ readValue="uint32", readStart=31102 ] // unit="kWh "
1.2.1 | 72 | 31103
1.2.1 | 73 | 31104 | 2 | Total Purchased Energy from Grid | RO | U32 | kWh | 10 |  |  |  |  | Thing data do073 "Total Purchased Energy from Grid" [ readValue="uint32", readStart=31104 ] // unit="kWh "
1.2.1 | 73 | 31105
1.2.1 | 74 | 31106 | 2 | Total Output Energy on Backup Port | RO | U32 | kWh | 10 |  |  |  |  | Thing data do074 "Total Output Energy on Backup Port" [ readValue="uint32", readStart=31106 ] // unit="kWh "
1.2.1 | 74 | 31107
1.2.1 | 75 | 31108 | 2 | Total Battery Charging Energy | RO | U32 | kWh | 10 |  |  |  |  | Thing data do075 "Total Battery Charging Energy " [ readValue="uint32", readStart=31108 ] // unit="kWh "
1.2.1 | 75 | 31109
1.2.1 | 76 | 31110 | 2 | Total Battery Discharging Energy | RO | U32 | kWh | 10 |  |  |  |  | Thing data do076 "Total Battery Discharging Energy" [ readValue="uint32", readStart=31110 ] // unit="kWh "
1.2.1 | 76 | 31111
1.2.1 | 77 | 31112 | 2 | Total PV Generation | RO | U32 | kWh | 10 |  |  |  |  | Thing data do077 "Total PV Generation" [ readValue="uint32", readStart=31112 ] // unit="kWh "
1.2.1 | 77 | 31113
1.2.1 | 78 | 31114 | 2 | Total Load Consumption | RO | U32 | kWh | 10 |  |  |  |  | Thing data do078 "Total Load Consumption" [ readValue="uint32", readStart=31114 ] // unit="kWh "
1.2.1 | 78 | 31115
1.2.1 | 79 | 31118 | 2 | Total Energy Purchased from Grid at Inverter Side | RO | U32 | kWh | 10 |  |  |  |  | Thing data do079 "Total Energy Purchased from Grid at Inverter Side" [ readValue="uint32", readStart=31118 ] // unit="kWh "
1.2.1 | 79 | 31119
1.2.1 | 80 | 32000 | 1 | Battery Type Codes | RO | U16 | N/A | 1 |  |  |  |  | Thing data do080 "Battery Type Codes" [ readValue="uint16", readStart=32000 ] // unit="N/A "
1.2.1 | 81 | 32001 | 1 | Battery strings | RO | U16 | N/A | 1 |  |  |  |  | Thing data do081 "Battery strings " [ readValue="uint16", readStart=32001 ] // unit="N/A "
1.2.1 | 82 | 32002 | 1 | Battery protocol | RO | U16 | N/A | 1 |  |  |  |  | Thing data do082 "Battery protocol " [ readValue="uint16", readStart=32002 ] // unit="N/A "
1.2.1 | 83 | 32003 | 1 | Software Version | RO | U16 | N/A | 1 |  |  |  |  | Thing data do083 "Software Version " [ readValue="uint16", readStart=32003 ] // unit="N/A "
1.2.1 | 84 | 32004 | 1 | Hardware Version | RO | U16 | N/A | 1 |  |  |  |  | Thing data do084 "Hardware Version " [ readValue="uint16", readStart=32004 ] // unit="N/A "
1.2.1 | 85 | 32005 | 1 | BMS Charge Imax | RO | U16 | A | 10 |  |  |  |  | Thing data do085 "BMS Charge Imax " [ readValue="uint16", readStart=32005 ] // unit="A "
1.2.1 | 86 | 32006 | 1 | BMS Discharge Imax | RO | U16 | A | 10 |  |  |  |  | Thing data do086 "BMS Discharge Imax" [ readValue="uint16", readStart=32006 ] // unit="A "
1.2.1 | 87 | 33000 | 1 | SOC | RO | U16 | % | 100 |  |  |  |  | Thing data do087 "SOC " [ readValue="uint16", readStart=33000 ] // unit="% "
1.2.1 | 88 | 33001 | 1 | SOH | RO | U16 | % | 100 |  |  |  |  | Thing data do088 "SOH " [ readValue="uint16", readStart=33001 ] // unit="% "
1.2.1 | 89 | 33002 | 1 | BMS Status | RO | U16 | N/A | 1 |  |  |  |  | Thing data do089 "BMS Status " [ readValue="uint16", readStart=33002 ] // unit="N/A "
1.2.1 | 90 | 33003 | 1 | BMS Pack Temperature | RO | U16 | °C | 10 |  |  |  |  | Thing data do090 "BMS Pack Temperature" [ readValue="uint16", readStart=33003 ] // unit="°C"
1.2.1 | 91 | 33008 | 1 | Max Cell Temperature ID | RO | U16 | N/A | 1 |  |  |  |  | Thing data do091 "Max Cell Temperature ID" [ readValue="uint16", readStart=33008 ] // unit="N/A "
1.2.1 | 92 | 33009 | 1 | Max Cell Temperature | RO | U16 | °C | 10 |  |  |  |  | Thing data do092 "Max Cell Temperature" [ readValue="uint16", readStart=33009 ] // unit="°C"
1.2.1 | 93 | 33010 | 1 | Min Cell Temperature ID | RO | U16 | N/A | 1 |  |  |  |  | Thing data do093 "Min Cell Temperature ID" [ readValue="uint16", readStart=33010 ] // unit="N/A "
1.2.1 | 94 | 33011 | 1 | Min Cell Temperature | RO | U16 | °C | 10 |  |  |  |  | Thing data do094 "Min Cell Temperature" [ readValue="uint16", readStart=33011 ] // unit="°C"
1.2.1 | 95 | 33012 | 1 | Max Cell Voltage ID | RO | U16 | N/A | 1 |  |  |  |  | Thing data do095 "Max Cell Voltage ID" [ readValue="uint16", readStart=33012 ] // unit="N/A "
1.2.1 | 96 | 33013 | 1 | Max Cell Voltage | RO | U16 | V | 1000 |  |  |  |  | Thing data do096 "Max Cell Voltage " [ readValue="uint16", readStart=33013 ] // unit="V "
1.2.1 | 97 | 33014 | 1 | Min Cell Voltage ID | RO | U16 | N/A | 1 |  |  |  |  | Thing data do097 "Min Cell Voltage ID " [ readValue="uint16", readStart=33014 ] // unit="N/A "
1.2.1 | 98 | 33015 | 1 | Min Cell Voltage | RO | U16 | V | 1000 |  |  |  |  | Thing data do098 "Min Cell Voltage " [ readValue="uint16", readStart=33015 ] // unit="V "
1.2.1 | 99 | 33016 | 2 | BMS ERROR CODE | RO | U32 | N/A | 1 |  |  |  |  | Thing data do099 "BMS ERROR CODE" [ readValue="uint32", readStart=33016 ] // unit="N/A "
1.2.1 | 99 | 33017
1.2.1 | 100 | 33018 | 2 | BMS WARN CODE | RO | U32 | N/A | 1 |  |  |  |  | Thing data do0100 "BMS WARN CODE " [ readValue="uint32", readStart=33018 ] // unit="N/A "
1.2.1 | 100 | 33019
1.2.1 | 101 | 33020 | 1 | Charge Cutoff Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do0101 "Charge Cutoff Voltage" [ readValue="uint16", readStart=33020 ] // unit="V "
1.2.1 | 102 | 33021 | 1 | Charge Current Limit | RO | U16 | A | 10 |  |  |  |  | Thing data do0102 "Charge Current Limit" [ readValue="uint16", readStart=33021 ] // unit="A "
1.2.1 | 103 | 33022 | 1 | Discharge Cutoff Voltage | RO | U16 | V | 10 |  |  |  |  | Thing data do0103 "Discharge Cutoff Voltage" [ readValue="uint16", readStart=33022 ] // unit="V "
1.2.1 | 104 | 33023 | 1 | Discharge Current Limit | RO | U16 | A | 10 |  |  |  |  | Thing data do0104 "Discharge Current Limit" [ readValue="uint16", readStart=33023 ] // unit="A "
1.2.4 | 1 | 20000 | 1 | Inverter RTC date and time (Continuous read in) | RW | U16 | N/A | 1 | High Bit Year [19-99] Low Bit Month [1-12] | 1
1.2.4 | 2 | 20001 | 1 |  |  |  | N/A | 1 | High Bit Day [1-31] Low Bit Hour [0-23] | 1
1.2.4 | 3 | 20002 | 1 |  |  |  | N/A | 1 | High Bit Minute [0-59] Low Bit Second [0-59] | 1
1.2.4 | 4 | 25000 | 1 | Safety Code | RW | U16 | N/A | 1 | Please refer to table 3.10
1.2.4 | 5 | 25015 | 1 | Overload Method Setting | RW | U16 | N/A | 1 | 0: Rated 1: 110% OverLoading 2: Limit
1.2.4 | 6 | 25100 | 1 | Grid Injection Power Limit Switch | RW | U16 | N/A | 1 | 0:OFF 1:ON
1.2.4 | 7 | 25103 | 1 | Grid Injection Power Limit % Setting | RW | U16 | N/A | 1000 | [0.0%-100.0%]
1.2.4 | 8 | 25104 | 1 | Smart Meter COM Status | WO | U16 | N/A | 1 | 0: Meter abnormal 1: Meter normal
1.2.4 | 9 | 25105 | 2 | Pmeter on Phase A | WO | I32 | W | 1
1.2.4 | 10 | 25107 | 2 | Pmeter on Phase B | WO | I32 | W | 1
1.2.4 | 11 | 25109 | 2 | Pmeter on Phase C | WO | I32 | W | 1
1.2.4 | 12 | 25118 | 1 | Reactive power limit percentage | RW | I16 | N/A | 1000 | [-600, +600] accuracy to 0.1%
1.2.4 | 13 | 25120 | 1 | PF Setting | RW | I16 | N/A | 1000 | (-1000, 800]U[800, 1000]
1.2.4 | 14 | 25121 | 1 | Reactive power Control Mode | RW | U16 | N/A | 1 | 0: OFF 1: PF 2: Qt 3: Q(P 4: Q(U)
1.2.4 | 15 | 28000 | 1 | Fault recovery voltage lower limit | RW | U16 | V | 10 | 550 - 2300
1.2.4 | 16 | 28001 | 1 | Fault recovery voltage upper limit | RW | U16 | V | 10 | 2300-3000
1.2.4 | 17 | 28002 | 1 | Fault recovery frequency lower limit | RW | U16 | Hz | 100 | 4500-6500
1.2.4 | 18 | 28003 | 1 | Fault recovery frequency upper limit | RW | U16 | Hz | 100 | 4500-6500
1.2.4 | 19 | 28004 | 1 | Level-1 undervoltage protection threshold | RW | U16 | V | 10 | 550 - 2300
1.2.4 | 20 | 28005 | 1 | Level-1 undervoltage protection duration | RW | U16 | Prd | 1 | 1-50000
1.2.4 | 21 | 28006 | 1 | Level-1 overvoltage protection threshold | RW | U16 | V | 10 | 2300-3000
1.2.4 | 22 | 28007 | 1 | Level-1 overvoltage protection duration | RW | U16 | Prd | 1 | 1-50000
1.2.4 | 23 | 28012 | 1 | Level-1 underfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500
1.2.4 | 24 | 28013 | 1 | Level-1 underfrequency protection duration | RW | U16 | Prd | 1 | 1-50000
1.2.4 | 25 | 28014 | 1 | Level-1 overfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500
1.2.4 | 26 | 28015 | 1 | Level-1 overfrequency protection duration | RW | U16 | Prd | 1 | 1-50000
1.2.4 | 27 | 28101 | 1 | 10' overvoltage switch | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 28 | 28102 | 1 | 10' overvoltage threshold | RW | U16 | V | 10 | 2300-3000
1.2.4 | 29 | 50000 | 1 | Hybrid Inverter Working Mode Setting | RW | U16 | N/A | 1 | Please refer to table 3.6
1.2.4 | 30 | 50001 | 1 | Enable UPS Function Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 31 | 50004 | 1 | Off-grid Voltage Setting | RW | U16 | V | 10
1.2.4 | 32 | 50005 | 1 | Off-grid Frequency Setting | RW | U16 | Hz | 100 | [45.00-65.00]Hz
1.2.4 | 33 | 50006 | 1 | On-Grid Unbalanced Output Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 34 | 50007 | 1 | Peak Load Shifting Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 35 | 50009 | 1 | Max. Grid Power Value Setting | RW | U16 | kVA | 10
1.2.4 | 36 | 50010 | 1 | Parallel Master-Slave Sign | RW | U16 | N/A | 1 | 0: Independent Operating 1: Parallel (Slave) 2: Parallel (Master)
1.2.4 | 37 | 50202 | 1 | AC Power Scheduling Mode Setting | RW | U16 | N/A | 1 | 0: Off 1: Total Power Setting, Register: 50203 2: Power Setting on each Phase, Registers: 5020450206
1.2.4 | 38 | 50203 | 1 | Total AC Power Scheduling Setting | RW | I16 | kW | 100 | Total AC Power Scheduling Setting
1.2.4 | 39 | 50204 | 1 | Phase A Power Scheduling Setting | RW | I16 | kW | 100 | Phase A Power Scheduling Setting
1.2.4 | 40 | 50205 | 1 | Phase B Power Scheduling Setting | RW | I16 | kW | 100 | Phase B Power Scheduling Setting
1.2.4 | 41 | 50206 | 1 | Phase C Power Scheduling Setting | RW | I16 | kW | 100 | Phase C Power Scheduling Setting
1.2.4 | 42 | 50207 | 1 | Battery Power Scheduling Setting | RW | I16 | kW | 100
1.2.4 | 43 | 50208 | 1 | Max. AC Power Limit Setting | RW | I16 | kW | 100
1.2.4 | 44 | 50209 | 1 | Min. AC Power Limit Setting | RW | I16 | kW | 100
1.2.4 | 45 | 50210 | 1 | Priority of Power Output Setting | RW | U16 | NA | 1 | 0: PV Output Priority 1: Battery Output Priority
1.2.4 | 46 | 50211 | 1 | PV Power Scheduling Setting | RW | U16 | kW | 100
1.2.4 | 47 | 52500 | 1 | Battery Configuration | RW | U16 | N/A | 1 | Please refer to table 3.7
1.2.4 | 48 | 52501 | 1 | Battery Protocol configuration | RW | U16 | N/A | 1
1.2.4 | 49 | 52502 | 1 | On-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 50 | 52503 | 1 | On-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%]
1.2.4 | 51 | 52504 | 1 | Off-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON
1.2.4 | 52 | 52505 | 1 | Off-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%]
1.2.4 | 53 | 53006 | 1 | Period Enable Flag | RW | U16 | N/A | 1 | bit0- bit5 stands for period1-period6, bit7-bit15 reserved; 0: disable 1: enable | 1
1.2.4 | 54 | 53007 | 1 | Charge/Discharge Setting | RW | U16 | N/A | 1 | Period1: 0:NONE 1:charge 2:discharge
1.2.4 | 55 | 53008 | 1 | Battery Charge By | RW | U16 | N/A | 1 | Period1: 0:PV 1:PV+GRID
1.2.4 | 56 | 53009 | 1 | rsved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF
1.2.4 | 57 | 53010 | 1 | Power Limit | RW | U16 | N/A | 1000 | Period1: [0.0-100.0%]
1.2.4 | 58 | 53011 | 1 | rsved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF
1.2.4 | 59 | 53012 | 1 | Start Time | RW | U16 | N/A | 1 | Period1: High 8bits(Hour): [0,23] Low 8bits(Mins): [0,59]
1.2.4 | 60 | 53013 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 61 | 53014 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period2 Note Same as Period1
1.2.4 | 62 | 53015 | 1 | Battery Charge By | RW | U16 | N/A | 1
1.2.4 | 63 | 53016 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 64 | 53017 | 1 | Power Limit | RW | U16 | N/A | 1000
1.2.4 | 65 | 53018 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 66 | 53019 | 1 | Start Time | RW | U16 | N/A | 1
1.2.4 | 67 | 53020 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 68 | 53021 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period3 Note Same as Period1
1.2.4 | 69 | 53022 | 1 | Battery Charge By | RW | U16 | N/A | 1
1.2.4 | 70 | 53023 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 71 | 53024 | 1 | Power Limit | RW | U16 | N/A | 1000
1.2.4 | 72 | 53025 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 73 | 53026 | 1 | Start Time | RW | U16 | N/A | 1
1.2.4 | 74 | 53027 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 75 | 53028 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period4 Note Same as Period1
1.2.4 | 76 | 53029 | 1 | Battery Charge By | RW | U16 | N/A | 1
1.2.4 | 77 | 53030 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 78 | 53031 | 1 | Power Limit | RW | U16 | N/A | 1000
1.2.4 | 79 | 53032 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 80 | 53033 | 1 | Start Time | RW | U16 | N/A | 1
1.2.4 | 81 | 53034 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 82 | 53035 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period5 Note Same as Period1
1.2.4 | 83 | 53036 | 1 | Battery Charge By | RW | U16 | N/A | 1
1.2.4 | 84 | 53037 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 85 | 53038 | 1 | Power Limit | RW | U16 | N/A | 1000
1.2.4 | 86 | 53039 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 87 | 53040 | 1 | Start Time | RW | U16 | N/A | 1
1.2.4 | 88 | 53041 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 89 | 53042 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period6 Note Same as Period1
1.2.4 | 90 | 53043 | 1 | Battery Charge By | RW | U16 | N/A | 1
1.2.4 | 91 | 53044 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 92 | 53045 | 1 | Power Limit | RW | U16 | N/A | 1000
1.2.4 | 93 | 53046 | 1 | rsved | RW | U16 | N/A | 1
1.2.4 | 94 | 53047 | 1 | Start Time | RW | U16 | N/A | 1
1.2.4 | 95 | 53048 | 1 | Stop Time | RW | U16 | N/A | 1
1.2.4 | 96 | 53500 | 8 | BMSVersion | WO | STR | N/A | 1 | Only for BMS access to EMS
1.2.4 | 97 | 53508 | 1 | BMS Status | WO | U16 | N/A | 1 | Please refer to Table 3.8 Only for BMS access to EMS
1.2.4 | 98 | 53509 | 2 | BMS ErrorCode | WO | U32 | N/A | 1 | Please refer to Table 3.9 Only for BMS access to EMS
1.2.4 | 99 | 53511 | 2 | BMS Protection Code | WO | U32 | N/A | 1
1.2.4 | 100 | 53513 | 2 | BMS WarnCode | WO | U32 | N/A | 1
1.2.4 | 101 | 53515 | 1 | BMSChargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS
1.2.4 | 102 | 53516 | 1 | BMSChargeCurrMax | WO | U16 | A | 10
1.2.4 | 103 | 53517 | 1 | BMSDishargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS
1.2.4 | 104 | 53518 | 1 | BMSDishargeCurrMax | WO | U16 | A | 10
1.2.4 | 105 | 53519 | 1 | BMSBatSOC | WO | U16 | % | 100
1.2.4 | 106 | 53520 | 1 | BMSBatSOH | WO | U16 | % | 100
1.2.4 | 107 | 53521 | 1 | BMSBatVoltage | WO | U16 | V | 10
1.2.4 | 108 | 53522 | 1 | BMSBatCurrent | WO | I16 | A | 10
1.2.4 | 109 | 53523 | 1 | BMSBatTemp | WO | I16 | °C | 10
1.2.5 | 1 | 50200 | 1 | Off-grid function Switch | WO | U16 | N/A | 1 | 0:OFF 1:ON
1.2.5 | 2 | 50201 | 1 | Clear Off-grid Over-loading Protection Flag | WO | U16 | N/A | 1 | Write 1 to clear

## RW Registers
No. | Address | Bytes | Function Description | R/W | Type | Unit | Accuracy | Note
1 | 20000 | 1 | Inverter RTC date and time (Continuous read in) | RW | U16 | N/A | 1 | High Bit Year [19-99] Low Bit Month [1-12] | Thing data do01 "Inverter RTC date and time (Continuous read in)" [ readValue="uint16", readStart=20000, writeValueType="uint16", writeStart=20000, writeType="holding" ] // unit="N/A "
2 | 20001 | 1 |  |  |  | N/A | 1 | High Bit Day [1-31] Low Bit Hour [0-23] | #N/A
3 | 20002 | 1 |  |  |  | N/A | 1 | High Bit Minute [0-59] Low Bit Second [0-59] | #N/A
4 | 25000 | 1 | Safety Code | RW | U16 | N/A | 1 | Please refer to table 3.10 | Thing data do04 "Safety Code " [ readValue="uint16", readStart=25000, writeValueType="uint16", writeStart=25000, writeType="holding" ] // unit="N/A "
5 | 25015 | 1 | Overload Method Setting | RW | U16 | N/A | 1 | 0: Rated 1: 110% OverLoading 2: Limit | Thing data do05 "Overload Method Setting" [ readValue="uint16", readStart=25015, writeValueType="uint16", writeStart=25015, writeType="holding" ] // unit="N/A "
6 | 25100 | 1 | Grid Injection Power Limit Switch | RW | U16 | N/A | 1 | 0:OFF 1:ON | Thing data do06 "Grid Injection Power Limit Switch" [ readValue="uint16", readStart=25100, writeValueType="uint16", writeStart=25100, writeType="holding" ] // unit="N/A "
7 | 25103 | 1 | Grid Injection Power Limit % Setting | RW | U16 | N/A | 1000 | [0.0%-100.0%] | Thing data do07 "Grid Injection Power Limit % Setting " [ readValue="uint16", readStart=25103, writeValueType="uint16", writeStart=25103, writeType="holding" ] // unit="N/A "
8 | 25104 | 1 | Smart Meter COM Status | WO | U16 | N/A | 1 | 0: Meter abnormal 1: Meter normal | Thing data do08 "Smart Meter COM Status" [ readValue="uint16", readStart=25104, writeValueType="uint16", writeStart=25104, writeType="holding" ] // unit="N/A "
9 | 25105 | 2 | Pmeter on Phase A | WO | I32 | W | 1 |  | Thing data do09 "Pmeter on Phase A" [ readValue="int32", readStart=25105, writeValueType="int32", writeStart=25105, writeType="holding" ] // unit="W "
10 | 25107 | 2 | Pmeter on Phase B | WO | I32 | W | 1 |  | Thing data do010 "Pmeter on Phase B" [ readValue="int32", readStart=25107, writeValueType="int32", writeStart=25107, writeType="holding" ] // unit="W "
11 | 25109 | 2 | Pmeter on Phase C | WO | I32 | W | 1 |  | Thing data do011 "Pmeter on Phase C" [ readValue="int32", readStart=25109, writeValueType="int32", writeStart=25109, writeType="holding" ] // unit="W "
12 | 25118 | 1 | Reactive power limit percentage | RW | I16 | N/A | 1000 | [-600, +600] accuracy to 0.1% | Thing data do012 "Reactive power limit percentage" [ readValue="int16", readStart=25118, writeValueType="int16", writeStart=25118, writeType="holding" ] // unit="N/A "
13 | 25120 | 1 | PF Setting | RW | I16 | N/A | 1000 | (-1000, 800]U[800, 1000] | Thing data do013 "PF Setting " [ readValue="int16", readStart=25120, writeValueType="int16", writeStart=25120, writeType="holding" ] // unit="N/A "
14 | 25121 | 1 | Reactive power Control Mode | RW | U16 | N/A | 1 | 0: OFF 1: PF 2: Qt 3: Q(P 4: Q(U) | Thing data do014 "Reactive power Control Mode " [ readValue="uint16", readStart=25121, writeValueType="uint16", writeStart=25121, writeType="holding" ] // unit="N/A "
15 | 28000 | 1 | Fault recovery voltage lower limit | RW | U16 | V | 10 | 550 - 2300 | Thing data do015 "Fault recovery voltage lower limit" [ readValue="uint16", readStart=28000, writeValueType="uint16", writeStart=28000, writeType="holding" ] // unit="V "
16 | 28001 | 1 | Fault recovery voltage upper limit | RW | U16 | V | 10 | 2300-3000 | Thing data do016 "Fault recovery voltage upper limit" [ readValue="uint16", readStart=28001, writeValueType="uint16", writeStart=28001, writeType="holding" ] // unit="V "
17 | 28002 | 1 | Fault recovery frequency lower limit | RW | U16 | Hz | 100 | 4500-6500 | Thing data do017 "Fault recovery frequency lower limit " [ readValue="uint16", readStart=28002, writeValueType="uint16", writeStart=28002, writeType="holding" ] // unit="Hz "
18 | 28003 | 1 | Fault recovery frequency upper limit | RW | U16 | Hz | 100 | 4500-6500 | Thing data do018 "Fault recovery frequency upper limit " [ readValue="uint16", readStart=28003, writeValueType="uint16", writeStart=28003, writeType="holding" ] // unit="Hz "
19 | 28004 | 1 | Level-1 undervoltage protection threshold | RW | U16 | V | 10 | 550 - 2300 | Thing data do019 "Level-1 undervoltage protection threshold " [ readValue="uint16", readStart=28004, writeValueType="uint16", writeStart=28004, writeType="holding" ] // unit="V "
20 | 28005 | 1 | Level-1 undervoltage protection duration | RW | U16 | Prd | 1 | 1-50000 | Thing data do020 "Level-1 undervoltage protection duration " [ readValue="uint16", readStart=28005, writeValueType="uint16", writeStart=28005, writeType="holding" ] // unit="Prd "
21 | 28006 | 1 | Level-1 overvoltage protection threshold | RW | U16 | V | 10 | 2300-3000 | Thing data do021 "Level-1 overvoltage protection threshold " [ readValue="uint16", readStart=28006, writeValueType="uint16", writeStart=28006, writeType="holding" ] // unit="V "
22 | 28007 | 1 | Level-1 overvoltage protection duration | RW | U16 | Prd | 1 | 1-50000 | Thing data do022 "Level-1 overvoltage protection duration " [ readValue="uint16", readStart=28007, writeValueType="uint16", writeStart=28007, writeType="holding" ] // unit="Prd "
23 | 28012 | 1 | Level-1 underfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500 | Thing data do023 "Level-1 underfrequency protection threshold" [ readValue="uint16", readStart=28012, writeValueType="uint16", writeStart=28012, writeType="holding" ] // unit="Hz "
24 | 28013 | 1 | Level-1 underfrequency protection duration | RW | U16 | Prd | 1 | 1-50000 | Thing data do024 "Level-1 underfrequency protection duration" [ readValue="uint16", readStart=28013, writeValueType="uint16", writeStart=28013, writeType="holding" ] // unit="Prd "
25 | 28014 | 1 | Level-1 overfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500 | Thing data do025 "Level-1 overfrequency protection threshold " [ readValue="uint16", readStart=28014, writeValueType="uint16", writeStart=28014, writeType="holding" ] // unit="Hz "
26 | 28015 | 1 | Level-1 overfrequency protection duration | RW | U16 | Prd | 1 | 1-50000 | Thing data do026 "Level-1 overfrequency protection duration " [ readValue="uint16", readStart=28015, writeValueType="uint16", writeStart=28015, writeType="holding" ] // unit="Prd "
| 28101 | 1 | 10' overvoltage switch | RW | U16 | N/A | 1 | 0: OFF 1: ON
| 28102 | 1 | 10' overvoltage threshold | RW | U16 | V | 10 | 2300-3000
27 | 50000 | 1 | Hybrid Inverter Working Mode Setting | RW | U16 | N/A | 1 | Please refer to table 3.6 | Thing data do027 "Hybrid Inverter Working Mode Setting " [ readValue="uint16", readStart=50000, writeValueType="uint16", writeStart=50000, writeType="holding" ] // unit="N/A "
28 | 50001 | 1 | Enable UPS Function Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON | Thing data do028 "Enable UPS Function Switch" [ readValue="uint16", readStart=50001, writeValueType="uint16", writeStart=50001, writeType="holding" ] // unit="N/A "
29 | 50004 | 1 | Off-grid Voltage Setting | RW | U16 | V | 10 |  | Thing data do029 "Off-grid Voltage Setting " [ readValue="uint16", readStart=50004, writeValueType="uint16", writeStart=50004, writeType="holding" ] // unit="V "
30 | 50005 | 1 | Off-grid Frequency Setting | RW | U16 | Hz | 100 | [45.00-65.00]Hz | Thing data do030 "Off-grid Frequency Setting " [ readValue="uint16", readStart=50005, writeValueType="uint16", writeStart=50005, writeType="holding" ] // unit="Hz "
31 | 50006 | 1 | On-Grid Unbalanced Output Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON | Thing data do031 "On-Grid Unbalanced Output Switch " [ readValue="uint16", readStart=50006, writeValueType="uint16", writeStart=50006, writeType="holding" ] // unit="N/A "
32 | 50007 | 1 | Peak Load Shifting Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON | Thing data do032 "Peak Load Shifting Switch " [ readValue="uint16", readStart=50007, writeValueType="uint16", writeStart=50007, writeType="holding" ] // unit="N/A "
33 | 50009 | 1 | Max. Grid Power Value Setting | RW | U16 | kVA | 10 |  | Thing data do033 "Max. Grid Power Value Setting " [ readValue="uint16", readStart=50009, writeValueType="uint16", writeStart=50009, writeType="holding" ] // unit="kVA "
34 | 50010 | 1 | Parallel Master-Slave Sign | RW | U16 | N/A | 1 | 0: Independent Operating 1: Parallel (Slave) 2: Parallel (Master) | Thing data do034 "Parallel Master-Slave Sign " [ readValue="uint16", readStart=50010, writeValueType="uint16", writeStart=50010, writeType="holding" ] // unit="N/A "
35 | 50202 | 1 | AC Power Scheduling Mode Setting | RW | U16 | N/A | 1 | 0: Off 1: Total Power Setting, Register: 50203 2: Power Setting on each Phase, Registers: 5020450206 | Thing data do035 "AC Power Scheduling Mode Setting" [ readValue="uint16", readStart=50202, writeValueType="uint16", writeStart=50202, writeType="holding" ] // unit="N/A "
36 | 50203 | 1 | Total AC Power Scheduling Setting | RW | I16 | kW | 100 | Total AC Power Scheduling Setting | Thing data do036 "Total AC Power Scheduling Setting " [ readValue="int16", readStart=50203, writeValueType="int16", writeStart=50203, writeType="holding" ] // unit="kW "
37 | 50204 | 1 | Phase A Power Scheduling Setting | RW | I16 | kW | 100 | Phase A Power Scheduling Setting | Thing data do037 "Phase A Power Scheduling Setting" [ readValue="int16", readStart=50204, writeValueType="int16", writeStart=50204, writeType="holding" ] // unit="kW "
38 | 50205 | 1 | Phase B Power Scheduling Setting | RW | I16 | kW | 100 | Phase B Power Scheduling Setting | Thing data do038 "Phase B Power Scheduling Setting" [ readValue="int16", readStart=50205, writeValueType="int16", writeStart=50205, writeType="holding" ] // unit="kW "
39 | 50206 | 1 | Phase C Power Scheduling Setting | RW | I16 | kW | 100 | Phase C Power Scheduling Setting | Thing data do039 "Phase C Power Scheduling Setting" [ readValue="int16", readStart=50206, writeValueType="int16", writeStart=50206, writeType="holding" ] // unit="kW "
40 | 50207 | 1 | Battery Power Scheduling Setting | RW | I16 | kW | 100 |  | Thing data do040 "Battery Power Scheduling Setting" [ readValue="int16", readStart=50207, writeValueType="int16", writeStart=50207, writeType="holding" ] // unit="kW "
41 | 50208 | 1 | Max. AC Power Limit Setting | RW | I16 | kW | 100 |  | Thing data do041 "Max. AC Power Limit Setting" [ readValue="int16", readStart=50208, writeValueType="int16", writeStart=50208, writeType="holding" ] // unit="kW "
42 | 50209 | 1 | Min. AC Power Limit Setting | RW | I16 | kW | 100 |  | Thing data do042 "Min. AC Power Limit Setting " [ readValue="int16", readStart=50209, writeValueType="int16", writeStart=50209, writeType="holding" ] // unit="kW "
43 | 50210 | 1 | Priority of Power Output Setting | RW | U16 | NA | 1 | 0: PV Output Priority 1: Battery Output Priority | Thing data do043 "Priority of Power Output Setting " [ readValue="uint16", readStart=50210, writeValueType="uint16", writeStart=50210, writeType="holding" ] // unit="NA "
44 | 50211 | 1 | PV Power Scheduling Setting | RW | U16 | kW | 100 |  | Thing data do044 "PV Power Scheduling Setting" [ readValue="uint16", readStart=50211, writeValueType="uint16", writeStart=50211, writeType="holding" ] // unit="kW "
45 | 52500 | 1 | Battery Configuration | RW | U16 | N/A | 1 | Please refer to table 3.7 | Thing data do045 "Battery Configuration " [ readValue="uint16", readStart=52500, writeValueType="uint16", writeStart=52500, writeType="holding" ] // unit="N/A "
46 | 52501 | 1 | Battery Protocol configuration | RW | U16 | N/A | 1 |  | Thing data do046 "Battery Protocol configuration " [ readValue="uint16", readStart=52501, writeValueType="uint16", writeStart=52501, writeType="holding" ] // unit="N/A "
47 | 52502 | 1 | On-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON | Thing data do047 "On-grid SOC Protection" [ readValue="uint16", readStart=52502, writeValueType="uint16", writeStart=52502, writeType="holding" ] // unit="N/A "
48 | 52503 | 1 | On-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%] | Thing data do048 "On-grid Battery End SOC" [ readValue="uint16", readStart=52503, writeValueType="uint16", writeStart=52503, writeType="holding" ] // unit="N/A "
49 | 52504 | 1 | Off-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON | Thing data do049 "Off-grid SOC Protection" [ readValue="uint16", readStart=52504, writeValueType="uint16", writeStart=52504, writeType="holding" ] // unit="N/A "
50 | 52505 | 1 | Off-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%] | Thing data do050 "Off-grid Battery End SOC" [ readValue="uint16", readStart=52505, writeValueType="uint16", writeStart=52505, writeType="holding" ] // unit="N/A "
51 | 53006 | 1 | Period Enable Flag | RW | U16 | N/A | 1 | bit0- bit5 stands for period1-period6, bit7-bit15 reserved; 0: disable 1: enable | Thing data do051 "Period Enable Flag " [ readValue="uint16", readStart=53006, writeValueType="uint16", writeStart=53006, writeType="holding" ] // unit="N/A "
52 | 53007 | 1 | Charge/Discharge Setting | RW | U16 | N/A | 1 | Period1: 0:NONE 1:charge 2:discharge | Thing data do052 "Charge/Discharge Setting " [ readValue="uint16", readStart=53007, writeValueType="uint16", writeStart=53007, writeType="holding" ] // unit="N/A "
53 | 53008 | 1 | Battery Charge By | RW | U16 | N/A | 1 | Period1: 0:PV 1:PV+GRID | Thing data do053 "Battery Charge By " [ readValue="uint16", readStart=53008, writeValueType="uint16", writeStart=53008, writeType="holding" ] // unit="N/A "
54 | 53009 | 1 | rsved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF | Thing data do054 "rsved " [ readValue="uint16", readStart=53009, writeValueType="uint16", writeStart=53009, writeType="holding" ] // unit="N/A "
55 | 53010 | 1 | Power Limit | RW | U16 | N/A | 1000 | Period1: [0.0-100.0%] | Thing data do055 "Power Limit " [ readValue="uint16", readStart=53010, writeValueType="uint16", writeStart=53010, writeType="holding" ] // unit="N/A "
56 | 53011 | 1 | rsved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF | Thing data do056 "rsved " [ readValue="uint16", readStart=53011, writeValueType="uint16", writeStart=53011, writeType="holding" ] // unit="N/A "
57 | 53012 | 1 | Start Time | RW | U16 | N/A | 1 | Period1: High 8bits(Hour): [0,23] Low 8bits(Mins): [0,59] | Thing data do057 "Start Time " [ readValue="uint16", readStart=53012, writeValueType="uint16", writeStart=53012, writeType="holding" ] // unit="N/A "
58 | 53013 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do058 "Stop Time " [ readValue="uint16", readStart=53013, writeValueType="uint16", writeStart=53013, writeType="holding" ] // unit="N/A "
59 | 53014 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period2 Note Same as Period1 | Thing data do059 "Charge/Discharge " [ readValue="uint16", readStart=53014, writeValueType="uint16", writeStart=53014, writeType="holding" ] // unit="N/A "
60 | 53015 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  | Thing data do060 "Battery Charge By " [ readValue="uint16", readStart=53015, writeValueType="uint16", writeStart=53015, writeType="holding" ] // unit="N/A "
61 | 53016 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do061 "rsved " [ readValue="uint16", readStart=53016, writeValueType="uint16", writeStart=53016, writeType="holding" ] // unit="N/A "
62 | 53017 | 1 | Power Limit | RW | U16 | N/A | 1000 |  | Thing data do062 "Power Limit " [ readValue="uint16", readStart=53017, writeValueType="uint16", writeStart=53017, writeType="holding" ] // unit="N/A "
63 | 53018 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do063 "rsved " [ readValue="uint16", readStart=53018, writeValueType="uint16", writeStart=53018, writeType="holding" ] // unit="N/A "
64 | 53019 | 1 | Start Time | RW | U16 | N/A | 1 |  | Thing data do064 "Start Time " [ readValue="uint16", readStart=53019, writeValueType="uint16", writeStart=53019, writeType="holding" ] // unit="N/A "
65 | 53020 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do065 "Stop Time " [ readValue="uint16", readStart=53020, writeValueType="uint16", writeStart=53020, writeType="holding" ] // unit="N/A "
66 | 53021 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period3 Note Same as Period1 | Thing data do066 "Charge/Discharge " [ readValue="uint16", readStart=53021, writeValueType="uint16", writeStart=53021, writeType="holding" ] // unit="N/A "
67 | 53022 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  | Thing data do067 "Battery Charge By " [ readValue="uint16", readStart=53022, writeValueType="uint16", writeStart=53022, writeType="holding" ] // unit="N/A "
68 | 53023 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do068 "rsved " [ readValue="uint16", readStart=53023, writeValueType="uint16", writeStart=53023, writeType="holding" ] // unit="N/A "
69 | 53024 | 1 | Power Limit | RW | U16 | N/A | 1000 |  | Thing data do069 "Power Limit " [ readValue="uint16", readStart=53024, writeValueType="uint16", writeStart=53024, writeType="holding" ] // unit="N/A "
70 | 53025 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do070 "rsved " [ readValue="uint16", readStart=53025, writeValueType="uint16", writeStart=53025, writeType="holding" ] // unit="N/A "
71 | 53026 | 1 | Start Time | RW | U16 | N/A | 1 |  | Thing data do071 "Start Time " [ readValue="uint16", readStart=53026, writeValueType="uint16", writeStart=53026, writeType="holding" ] // unit="N/A "
72 | 53027 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do072 "Stop Time " [ readValue="uint16", readStart=53027, writeValueType="uint16", writeStart=53027, writeType="holding" ] // unit="N/A "
73 | 53028 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period4 Note Same as Period1 | Thing data do073 "Charge/Discharge " [ readValue="uint16", readStart=53028, writeValueType="uint16", writeStart=53028, writeType="holding" ] // unit="N/A "
74 | 53029 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  | Thing data do074 "Battery Charge By " [ readValue="uint16", readStart=53029, writeValueType="uint16", writeStart=53029, writeType="holding" ] // unit="N/A "
75 | 53030 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do075 "rsved " [ readValue="uint16", readStart=53030, writeValueType="uint16", writeStart=53030, writeType="holding" ] // unit="N/A "
76 | 53031 | 1 | Power Limit | RW | U16 | N/A | 1000 |  | Thing data do076 "Power Limit " [ readValue="uint16", readStart=53031, writeValueType="uint16", writeStart=53031, writeType="holding" ] // unit="N/A "
77 | 53032 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do077 "rsved " [ readValue="uint16", readStart=53032, writeValueType="uint16", writeStart=53032, writeType="holding" ] // unit="N/A "
78 | 53033 | 1 | Start Time | RW | U16 | N/A | 1 |  | Thing data do078 "Start Time " [ readValue="uint16", readStart=53033, writeValueType="uint16", writeStart=53033, writeType="holding" ] // unit="N/A "
79 | 53034 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do079 "Stop Time " [ readValue="uint16", readStart=53034, writeValueType="uint16", writeStart=53034, writeType="holding" ] // unit="N/A "
80 | 53035 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period5 Note Same as Period1 | Thing data do080 "Charge/Discharge " [ readValue="uint16", readStart=53035, writeValueType="uint16", writeStart=53035, writeType="holding" ] // unit="N/A "
81 | 53036 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  | Thing data do081 "Battery Charge By " [ readValue="uint16", readStart=53036, writeValueType="uint16", writeStart=53036, writeType="holding" ] // unit="N/A "
82 | 53037 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do082 "rsved " [ readValue="uint16", readStart=53037, writeValueType="uint16", writeStart=53037, writeType="holding" ] // unit="N/A "
83 | 53038 | 1 | Power Limit | RW | U16 | N/A | 1000 |  | Thing data do083 "Power Limit " [ readValue="uint16", readStart=53038, writeValueType="uint16", writeStart=53038, writeType="holding" ] // unit="N/A "
84 | 53039 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do084 "rsved " [ readValue="uint16", readStart=53039, writeValueType="uint16", writeStart=53039, writeType="holding" ] // unit="N/A "
85 | 53040 | 1 | Start Time | RW | U16 | N/A | 1 |  | Thing data do085 "Start Time " [ readValue="uint16", readStart=53040, writeValueType="uint16", writeStart=53040, writeType="holding" ] // unit="N/A "
86 | 53041 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do086 "Stop Time " [ readValue="uint16", readStart=53041, writeValueType="uint16", writeStart=53041, writeType="holding" ] // unit="N/A "
87 | 53042 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period6 Note Same as Period1 | Thing data do087 "Charge/Discharge " [ readValue="uint16", readStart=53042, writeValueType="uint16", writeStart=53042, writeType="holding" ] // unit="N/A "
88 | 53043 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  | Thing data do088 "Battery Charge By " [ readValue="uint16", readStart=53043, writeValueType="uint16", writeStart=53043, writeType="holding" ] // unit="N/A "
89 | 53044 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do089 "rsved " [ readValue="uint16", readStart=53044, writeValueType="uint16", writeStart=53044, writeType="holding" ] // unit="N/A "
90 | 53045 | 1 | Power Limit | RW | U16 | N/A | 1000 |  | Thing data do090 "Power Limit " [ readValue="uint16", readStart=53045, writeValueType="uint16", writeStart=53045, writeType="holding" ] // unit="N/A "
91 | 53046 | 1 | rsved | RW | U16 | N/A | 1 |  | Thing data do091 "rsved " [ readValue="uint16", readStart=53046, writeValueType="uint16", writeStart=53046, writeType="holding" ] // unit="N/A "
92 | 53047 | 1 | Start Time | RW | U16 | N/A | 1 |  | Thing data do092 "Start Time " [ readValue="uint16", readStart=53047, writeValueType="uint16", writeStart=53047, writeType="holding" ] // unit="N/A "
93 | 53048 | 1 | Stop Time | RW | U16 | N/A | 1 |  | Thing data do093 "Stop Time " [ readValue="uint16", readStart=53048, writeValueType="uint16", writeStart=53048, writeType="holding" ] // unit="N/A "
94 | 53500 | 8 | BMSVersion | WO | STR | N/A | 1 | Only for BMS access to EMS | Thing data do094 "BMSVersion " [ readValue="TODO", readStart=53500, writeValueType="TODO", writeStart=53500, writeType="holding" ] // unit="N/A "
95 | 53508 | 1 | BMS Status | WO | U16 | N/A | 1 | Please refer to Table 3.8 Only for BMS access to EMS | Thing data do095 "BMS Status " [ readValue="uint16", readStart=53508, writeValueType="uint16", writeStart=53508, writeType="holding" ] // unit="N/A "
96 | 53509 | 2 | BMS ErrorCode | WO | U32 | N/A | 1 | Please refer to Table 3.9 Only for BMS access to EMS | Thing data do096 "BMS ErrorCode " [ readValue="uint32", readStart=53509, writeValueType="uint32", writeStart=53509, writeType="holding" ] // unit="N/A "
97 | 53511 | 2 | BMS Protection Code | WO | U32 | N/A | 1 |  | Thing data do097 "BMS Protection Code" [ readValue="uint32", readStart=53511, writeValueType="uint32", writeStart=53511, writeType="holding" ] // unit="N/A "
98 | 53513 | 2 | BMS WarnCode | WO | U32 | N/A | 1 |  | Thing data do098 "BMS WarnCode " [ readValue="uint32", readStart=53513, writeValueType="uint32", writeStart=53513, writeType="holding" ] // unit="N/A "
99 | 53515 | 1 | BMSChargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS | Thing data do099 "BMSChargeVoltLimit " [ readValue="uint16", readStart=53515, writeValueType="uint16", writeStart=53515, writeType="holding" ] // unit="V "
100 | 53516 | 1 | BMSChargeCurrMax | WO | U16 | A | 10 |  | Thing data do0100 "BMSChargeCurrMax " [ readValue="uint16", readStart=53516, writeValueType="uint16", writeStart=53516, writeType="holding" ] // unit="A "
101 | 53517 | 1 | BMSDishargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS | Thing data do0101 "BMSDishargeVoltLimit " [ readValue="uint16", readStart=53517, writeValueType="uint16", writeStart=53517, writeType="holding" ] // unit="V "
102 | 53518 | 1 | BMSDishargeCurrMax | WO | U16 | A | 10 |  | Thing data do0102 "BMSDishargeCurrMax " [ readValue="uint16", readStart=53518, writeValueType="uint16", writeStart=53518, writeType="holding" ] // unit="A "
103 | 53519 | 1 | BMSBatSOC | WO | U16 | % | 100 |  | Thing data do0103 "BMSBatSOC " [ readValue="uint16", readStart=53519, writeValueType="uint16", writeStart=53519, writeType="holding" ] // unit="% "
104 | 53520 | 1 | BMSBatSOH | WO | U16 | % | 100 |  | Thing data do0104 "BMSBatSOH " [ readValue="uint16", readStart=53520, writeValueType="uint16", writeStart=53520, writeType="holding" ] // unit="% "
105 | 53521 | 1 | BMSBatVoltage | WO | U16 | V | 10 |  | Thing data do0105 "BMSBatVoltage" [ readValue="uint16", readStart=53521, writeValueType="uint16", writeStart=53521, writeType="holding" ] // unit="V "
106 | 53522 | 1 | BMSBatCurrent | WO | I16 | A | 10 |  | Thing data do0106 "BMSBatCurrent" [ readValue="int16", readStart=53522, writeValueType="int16", writeStart=53522, writeType="holding" ] // unit="A "
107 | 53523 | 1 | BMSBatTemp | WO | I16 | ? | 10 |  | Thing data do0107 "BMSBatTemp " [ readValue="int16", readStart=53523, writeValueType="int16", writeStart=53523, writeType="holding" ] // unit="? "

## Data Types
Solinteg Data Type | Modbus Binding Data Type
U16 | uint16
U32 | uint32
I16 | int16
I32 | int32
STR | TODO

## Working Mode
| 32768 | 16384 | 8192 | 4096 | 2048 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2 | 1
Bit | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
General Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 257
Economic Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 258
UPS Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 259
Off Grid Mode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512
EMS_ACCtrlMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 769
EMS_GeneralMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 770
EMS_BattCtrlMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 771
EMS_OffGridMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 772