## Registers
Table | No. | Address | Bytes | Function Description | R/W | Type | Unit | Accuracy | Note | manual definition | manual item type | transform | exclude | icon
1.2.1 | 1 | 10000 | 8 | Device SN | RO | STR | N/A | 1 | Read bytes to string | 1 | String |  |  | keyring
1.2.1 | 1 | 10001 | [7 empty] | 1 | String
1.2.1 | 1 | 10002 | [7 empty] | 1 | String
1.2.1 | 1 | 10003 | [7 empty] | 1 | String
1.2.1 | 1 | 10004 | [7 empty] | 1 | String
1.2.1 | 1 | 10005 | [7 empty] | 1 | String
1.2.1 | 1 | 10006 | [7 empty] | 1 | String
1.2.1 | 1 | 10007 | [7 empty] | 1 | String
1.2.1 | 2 | 10008 | 1 | Inverter Model | RO | U16 | N/A | 1 | Please refer to table 3.2 | 1 |  |  |  | keyring
1.2.1 | 3 | 10011 | 2 | Firmware Version | RO | U32 | N/A | 1 | Read bytes | 1 |  |  |  | settings
1.2.1 | 3 | 10012 | [7 empty] | 1
1.2.1 | 4 | 10100 | 1 | Date: Y/M | RO | U16 | N/A | 1 | Continuous read | 1 |  |  |  | calendar
1.2.1 | 5 | 10101 | 1 | Time: D/H | RO | U16 | N/A | 1 |  | 1 |  |  |  | calendar
1.2.1 | 6 | 10102 | 1 | Time: M/S | RO | U16 | N/A | 1 |  | 1 |  |  |  | calendar
1.2.1 | 7 | 10104 | 1 | Safety Code | RO | U16 | N/A | 1 |  |  |  | solinteg-saftey-code.js |  | f7:tag
1.2.1 | 8 | 10105 | 1 | Inverter Working Status | RO | U16 | N/A | 1 | 0: Wait for grid connection 1: Self-checking 2: On-grid generating 3: Device fault 4: Firmware upgrade 5: Off-grid generating |  |  | solinteg-inverter-working-status.map |  | settings
1.2.1 | 9 | 10112 | 2 | Fault FLAG1 | RO | U32 | N/A | 1 | Please refer to table 3.3 | 1 | Switch |  |  | error
1.2.1 | 9 | 10113 | [7 empty] | 1 | Switch
1.2.1 | 10 | 10114 | 2 | Fault FLAG2 | RO | U32 | N/A | 1 |  | 1 | Switch |  |  | error
1.2.1 | 10 | 10115 | [7 empty] | 1 | Switch
1.2.1 | 11 | 10120 | 2 | Fault FLAG3 | RO | U32 | N/A | 1 |  | 1 | Switch |  |  | error
1.2.1 | 11 | 10121 | [7 empty] | 1 | Switch
1.2.1 | 12 | 10994 | 2 | Pmeter on phase A | RO | I32 | kW | 1000 | [5 empty] | energy
1.2.1 | 12 | 10995
1.2.1 | 13 | 10996 | 2 | Pmeter on phase B | RO | I32 | kW | 1000 | [5 empty] | energy
1.2.1 | 13 | 10997
1.2.1 | 14 | 10998 | 2 | Pmeter on phase C | RO | I32 | kW | 1000 | [5 empty] | energy
1.2.1 | 14 | 10999
1.2.1 | 15 | 11000 | 2 | Pmeter of three phases | RO | I32 | kW | 1000 | [5 empty] | energy
1.2.1 | 15 | 11001
1.2.1 | 16 | 11002 | 2 | Total Grid-Injection Energy on Meter | RO | U32 | kWh | 100 | [5 empty] | energy
1.2.1 | 16 | 11003
1.2.1 | 17 | 11004 | 2 | Total Purchasing Energy from Grid on Meter | RO | U32 | kWh | 100 | [5 empty] | energy
1.2.1 | 17 | 11005
1.2.1 | 18 | 11006 | 1 | AB line voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 19 | 11007 | 1 | BC line voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 20 | 11008 | 1 | CA line voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 21 | 11009 | 1 | Phase A Voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 22 | 11010 | 1 | Phase A Current | RO | U16 | A | 10 | [5 empty] | energy
1.2.1 | 23 | 11011 | 1 | Phase B Voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 24 | 11012 | 1 | Phase B Current | RO | U16 | A | 10 | [5 empty] | energy
1.2.1 | 25 | 11013 | 1 | Phase C Voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 26 | 11014 | 1 | Phase C Current | RO | U16 | A | 10 | [5 empty] | energy
1.2.1 | 27 | 11015 | 1 | Grid Frequency | RO | U16 | Hz | 100 | [5 empty] | energy
1.2.1 | 28 | 11016 | 2 | Power AC | RO | I32 | kW | 1000 | [5 empty] | energy
1.2.1 | 28 | 11017
1.2.1 | 29 | 11018 | 2 | Energy today | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 29 | 11019
1.2.1 | 30 | 11020 | 2 | Energy total | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 30 | 11021
1.2.1 | 31 | 11022 | 2 | Total Generation Hours | RO | U32 | H | 1 | [5 empty] | time
1.2.1 | 31 | 11023
1.2.1 | 32 | 11028 | 2 | Total PV Input Power | RO | U32 | kW | 1000 | [5 empty] | energy
1.2.1 | 32 | 11029
1.2.1 | 33 | 11032 | 1 | Temp. 1 | RO | I16 | °C | 10 | [5 empty] | temperature
1.2.1 | 34 | 11033 | 1 | Temp. 2 | RO | I16 | °C | 10 | [5 empty] | temperature
1.2.1 | 35 | 11034 | 1 | Temp. 3 | RO | I16 | °C | 10 | [5 empty] | temperature
1.2.1 | 36 | 11035 | 1 | Temp. 4 | RO | I16 | °C | 10 | [5 empty] | temperature
1.2.1 | 37 | 11038 | 1 | PV1 Voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 38 | 11039 | 1 | PV1 Current | RO | U16 | A | 10 | [5 empty] | energy
1.2.1 | 39 | 11040 | 1 | PV2 Voltage | RO | U16 | V | 10 | [5 empty] | energy
1.2.1 | 40 | 11041 | 1 | PV2 Current | RO | U16 | A | 10 | [5 empty] | energy
1.2.1 | 41 | 11062 | 2 | PV1 Input Power | RO | U32 | kW | 1000 | [5 empty] | energy
1.2.1 | 41 | 11063
1.2.1 | 42 | 11064 | 2 | PV2 Input Power | RO | U32 | kW | 1000 | [5 empty] | energy
1.2.1 | 42 | 11065
1.2.1 | 43 | 18000 | 2 | ARM Fault FLAG1 | RO | U32 | N/A | 1 | Please refer to table 3.3 | 1 | Switch |  |  | error
1.2.1 | 43 | 18001 | [7 empty] | 1 | Switch
1.2.1 | 44 | 30200 | 1 | Backup A Voltage | RO | U16 | V | 10 | AC Voltage |  |  |  |  | energy
1.2.1 | 45 | 30201 | 1 | Backup A Current | RO | U16 | A | 10 | AC Current |  |  |  |  | energy
1.2.1 | 46 | 30202 | 1 | Backup A Frequency | RO | U16 | Hz | 100 | Frequency |  |  |  |  | energy
1.2.1 | 47 | 30204 | 2 | Backup A Power | RO | I32 | kW | 1000 | AC Active Power |  |  |  |  | energy
1.2.1 | 47 | 30205
1.2.1 | 48 | 30210 | 1 | Backup B Voltage | RO | U16 | V | 10 | AC Voltage |  |  |  |  | energy
1.2.1 | 49 | 30211 | 1 | Backup B Current | RO | U16 | A | 10 | AC Current |  |  |  |  | energy
1.2.1 | 50 | 30212 | 1 | Backup B Frequency | RO | U16 | Hz | 100 | Frequency |  |  |  |  | energy
1.2.1 | 51 | 30214 | 2 | Backup B Power | RO | I32 | kW | 1000 | AC Active Power |  |  |  |  | energy
1.2.1 | 51 | 30215
1.2.1 | 52 | 30220 | 1 | Backup C Voltage | RO | U16 | V | 10 | AC Voltage |  |  |  |  | energy
1.2.1 | 53 | 30221 | 1 | Backup C Current | RO | U16 | A | 10 | AC Current |  |  |  |  | energy
1.2.1 | 54 | 30222 | 1 | Backup C Frequency | RO | U16 | Hz | 100 | Frequency |  |  |  |  | energy
1.2.1 | 55 | 30224 | 2 | Backup C Power | RO | I32 | kW | 1000 | AC Active Power |  |  |  |  | energy
1.2.1 | 55 | 30225
1.2.1 | 56 | 30230 | 2 | Total Active Power | RO | I32 | kW | 1000 | Total Active Power |  |  |  |  | energy
1.2.1 | 56 | 20231
1.2.1 | 57 | 30236 | 2 | Phase A Active Power | RO | I32 | kW | 1000 | Phase A Active Power |  |  |  |  | energy
1.2.1 | 57 | 30237
1.2.1 | 58 | 30242 | 2 | Phase B Active Power | RO | I32 | kW | 1000 | Phase B Active Power |  |  |  |  | energy
1.2.1 | 58 | 30243
1.2.1 | 59 | 30248 | 2 | Phase C Active Power | RO | I32 | kW | 1000 | Phase C Active Power |  |  |  |  | energy
1.2.1 | 59 | 30249
1.2.1 | 60 | 30254 | 1 | Battery Voltage | RO | U16 | V | 10 | Battery Voltage |  |  |  |  | batterylevel
1.2.1 | 61 | 30255 | 1 | Battery Current | RO | I16 | A | 10 | Battery Current |  |  |  |  | batterylevel
1.2.1 | 62 | 30256 | 1 | Battery Mode | RO | U16 | N/A | 1 | 0: discharge 1: charge |  | Switch | solinteg-battery-mode.map |  | batterylevel
1.2.1 | 63 | 30258 | 2 | Battery Power | RO | I32 | kW | 1000 | Battery Power |  |  |  |  | batterylevel
1.2.1 | 63 | 30259
1.2.1 | 64 | 31000 | 1 | Daily Energy Injected to Grid | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 65 | 31001 | 1 | Daily Purchased Energy | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 66 | 31002 | 1 | Daily Energy Output on Backup | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 67 | 31003 | 1 | Daily Battery Charging Energy | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 68 | 31004 | 1 | Daily Battery Discharging | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 69 | 31005 | 1 | Daily PV Generation | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 70 | 31006 | 1 | Daily Load Consumption | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 71 | 31008 | 1 | Daily Energy Purchased from Grid at Inverter | RO | U16 | kWh | 10 | [5 empty] | energy
1.2.1 | 72 | 31102 | 2 | Total Energy Injected into Grid | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 72 | 31103
1.2.1 | 73 | 31104 | 2 | Total Purchased Energy from Grid | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 73 | 31105
1.2.1 | 74 | 31106 | 2 | Total Output Energy on Backup Port | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 74 | 31107
1.2.1 | 75 | 31108 | 2 | Total Battery Charging Energy | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 75 | 31109
1.2.1 | 76 | 31110 | 2 | Total Battery Discharging Energy | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 76 | 31111
1.2.1 | 77 | 31112 | 2 | Total PV Generation | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 77 | 31113
1.2.1 | 78 | 31114 | 2 | Total Load Consumption | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 78 | 31115
1.2.1 | 79 | 31118 | 2 | Total Energy Purchased from Grid at Inverter Side | RO | U32 | kWh | 10 | [5 empty] | energy
1.2.1 | 79 | 31119
1.2.1 | 80 | 32000 | 1 | Battery Type Codes | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 81 | 32001 | 1 | Battery strings | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 82 | 32002 | 1 | Battery protocol | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 83 | 32003 | 1 | Software Version | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 84 | 32004 | 1 | Hardware Version | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 85 | 32005 | 1 | BMS Charge Imax | RO | U16 | A | 10 | [5 empty] | batterylevel
1.2.1 | 86 | 32006 | 1 | BMS Discharge Imax | RO | U16 | A | 10 | [5 empty] | batterylevel
1.2.1 | 87 | 33000 | 1 | SOC | RO | U16 | % | 100 | [5 empty] | batterylevel
1.2.1 | 88 | 33001 | 1 | SOH | RO | U16 | % | 100 | [5 empty] | batterylevel
1.2.1 | 89 | 33002 | 1 | BMS Status | RO | U16 | N/A | 1 | [5 empty] | batterylevel
1.2.1 | 90 | 33003 | 1 | BMS Pack Temperature | RO | U16 | °C | 10 | [5 empty] | temperature
1.2.1 | 91 | 33008 | 1 | Max Cell Temperature ID | RO | U16 | N/A | 1 | [5 empty] | temperature
1.2.1 | 92 | 33009 | 1 | Max Cell Temperature | RO | U16 | °C | 10 | [5 empty] | temperature
1.2.1 | 93 | 33010 | 1 | Min Cell Temperature ID | RO | U16 | N/A | 1 | [5 empty] | temperature
1.2.1 | 94 | 33011 | 1 | Min Cell Temperature | RO | U16 | °C | 10 | [5 empty] | temperature
1.2.1 | 95 | 33012 | 1 | Max Cell Voltage ID | RO | U16 | N/A | 1 | [5 empty] | energy
1.2.1 | 96 | 33013 | 1 | Max Cell Voltage | RO | U16 | V | 1000 | [5 empty] | energy
1.2.1 | 97 | 33014 | 1 | Min Cell Voltage ID | RO | U16 | N/A | 1 | [5 empty] | energy
1.2.1 | 98 | 33015 | 1 | Min Cell Voltage | RO | U16 | V | 1000 | [5 empty] | energy
1.2.1 | 99 | 33016 | 2 | BMS ERROR CODE | RO | U32 | N/A | 1 | [5 empty] | error
1.2.1 | 99 | 33017
1.2.1 | 100 | 33018 | 2 | BMS WARN CODE | RO | U32 | N/A | 1 | [5 empty] | error
1.2.1 | 100 | 33019
1.2.1 | 101 | 33020 | 1 | Charge Cutoff Voltage | RO | U16 | V | 10 | [5 empty] | batterylevel
1.2.1 | 102 | 33021 | 1 | Charge Current Limit | RO | U16 | A | 10 | [5 empty] | batterylevel
1.2.1 | 103 | 33022 | 1 | Discharge Cutoff Voltage | RO | U16 | V | 10 | [5 empty] | batterylevel
1.2.1 | 104 | 33023 | 1 | Discharge Current Limit | RO | U16 | A | 10 | [5 empty] | batterylevel
1.2.4 | 1 | 20000 | 1 | Inverter RTC date and time (Continuous read in) | RW | U16 | N/A | 1 | High Bit Year [19-99] Low Bit Month [1-12] | 1 |  |  |  | calendar
1.2.4 | 2 | 20001 | 1 |  |  |  | N/A | 1 | High Bit Day [1-31] Low Bit Hour [0-23] | 1 |  |  |  | calendar
1.2.4 | 3 | 20002 | 1 |  |  |  | N/A | 1 | High Bit Minute [0-59] Low Bit Second [0-59] | 1 |  |  |  | calendar
1.2.4 | 4 | 25000 | 1 | Safety Code | RW | U16 | N/A | 1 | Please refer to table 3.10 |  |  |  |  | settings
1.2.4 | 5 | 25015 | 1 | Overload Method Setting | RW | U16 | N/A | 1 | 0: Rated 1: 110% OverLoading 2: Limit |  |  | solinteg-overload-method.map |  | energy
1.2.4 | 6 | 25100 | 1 | Grid Injection Power Limit Switch | RW | U16 | N/A | 1 | 0:OFF 1:ON |  | Switch |  |  | switch
1.2.4 | 7 | 25103 | 1 | Grid Injection Power Limit % Setting | RW | U16 | N/A | 1000 | [0.0%-100.0%] |  |  |  |  | energy
1.2.4 | 8 | 25104 | 1 | Smart Meter COM Status | WO | U16 | N/A | 1 | 0: Meter abnormal 1: Meter normal |  | Switch |  | 1 | status
1.2.4 | 9 | 25105 | 2 | Pmeter on Phase A | WO | I32 | W | 1 |  |  |  |  | 1 | energy
1.2.4 | 10 | 25107 | 2 | Pmeter on Phase B | WO | I32 | W | 1 |  |  |  |  | 1 | energy
1.2.4 | 11 | 25109 | 2 | Pmeter on Phase C | WO | I32 | W | 1 |  |  |  |  | 1 | energy
1.2.4 | 12 | 25118 | 1 | Reactive power limit percentage | RW | I16 | N/A | 1000 | [-600, +600] accuracy to 0.1% |  |  |  |  | energy
1.2.4 | 13 | 25120 | 1 | PF Setting | RW | I16 | N/A | 1000 | (-1000, 800]U[800, 1000] |  |  |  |  | energy
1.2.4 | 14 | 25121 | 1 | Reactive power Control Mode | RW | U16 | N/A | 1 | 0: OFF 1: PF 2: Qt 3: Q(P 4: Q(U) |  |  | solinteg-pwr-ctl.map |  | energy
1.2.4 | 15 | 28000 | 1 | Fault recovery voltage lower limit | RW | U16 | V | 10 | 550 - 2300 |  |  |  |  | error
1.2.4 | 16 | 28001 | 1 | Fault recovery voltage upper limit | RW | U16 | V | 10 | 2300-3000 |  |  |  |  | error
1.2.4 | 17 | 28002 | 1 | Fault recovery frequency lower limit | RW | U16 | Hz | 100 | 4500-6500 |  |  |  |  | error
1.2.4 | 18 | 28003 | 1 | Fault recovery frequency upper limit | RW | U16 | Hz | 100 | 4500-6500 |  |  |  |  | error
1.2.4 | 19 | 28004 | 1 | Level-1 undervoltage protection threshold | RW | U16 | V | 10 | 550 - 2300 |  |  |  |  | error
1.2.4 | 20 | 28005 | 1 | Level-1 undervoltage protection duration | RW | U16 | Prd | 1 | 1-50000 |  |  |  |  | error
1.2.4 | 21 | 28006 | 1 | Level-1 overvoltage protection threshold | RW | U16 | V | 10 | 2300-3000 |  |  |  |  | error
1.2.4 | 22 | 28007 | 1 | Level-1 overvoltage protection duration | RW | U16 | Prd | 1 | 1-50000 |  |  |  |  | error
1.2.4 | 23 | 28012 | 1 | Level-1 underfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500 |  |  |  |  | error
1.2.4 | 24 | 28013 | 1 | Level-1 underfrequency protection duration | RW | U16 | Prd | 1 | 1-50000 |  |  |  |  | error
1.2.4 | 25 | 28014 | 1 | Level-1 overfrequency protection threshold | RW | U16 | Hz | 100 | 4500-6500 |  |  |  |  | error
1.2.4 | 26 | 28015 | 1 | Level-1 overfrequency protection duration | RW | U16 | Prd | 1 | 1-50000 |  |  |  |  | error
1.2.4 | 27 | 28101 | 1 | 10m overvoltage switch | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | error
1.2.4 | 28 | 28102 | 1 | 10m overvoltage threshold | RW | U16 | V | 10 | 2300-3000 |  |  |  |  | error
1.2.4 | 29 | 50000 | 1 | Hybrid Inverter Working Mode Setting | RW | U16 | N/A | 1 | Please refer to table 3.6 |  |  | solinteg-working-mode.map |  | settings
1.2.4 | 30 | 50001 | 1 | Enable UPS Function Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | batterylevel
1.2.4 | 31 | 50004 | 1 | Off-grid Voltage Setting | RW | U16 | V | 10 | [5 empty] | energy
1.2.4 | 32 | 50005 | 1 | Off-grid Frequency Setting | RW | U16 | Hz | 100 | [45.00-65.00]Hz |  |  |  |  | energy
1.2.4 | 33 | 50006 | 1 | On-Grid Unbalanced Output Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | energy
1.2.4 | 34 | 50007 | 1 | Peak Load Shifting Switch | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | energy
1.2.4 | 35 | 50009 | 1 | Max. Grid Power Value Setting | RW | U16 | kVA | 10 | [5 empty] | energy
1.2.4 | 36 | 50010 | 1 | Parallel Master-Slave Sign | RW | U16 | N/A | 1 | 0: Independent Operating 1: Parallel (Slave) 2: Parallel (Master) |  |  | solinteg-ms.map |  | settings
1.2.4 | 37 | 50202 | 1 | AC Power Scheduling Mode Setting | RW | U16 | N/A | 1 | 0: Off 1: Total Power Setting, Register: 50203 2: Power Setting on each Phase, Registers: 5020450206 |  |  | solinteg-pwr-schdl.map |  | settings
1.2.4 | 38 | 50203 | 1 | Total AC Power Scheduling Setting | RW | I16 | kW | 100 | Total AC Power Scheduling Setting |  |  |  |  | energy
1.2.4 | 39 | 50204 | 1 | Phase A Power Scheduling Setting | RW | I16 | kW | 100 | Phase A Power Scheduling Setting |  |  |  |  | energy
1.2.4 | 40 | 50205 | 1 | Phase B Power Scheduling Setting | RW | I16 | kW | 100 | Phase B Power Scheduling Setting |  |  |  |  | energy
1.2.4 | 41 | 50206 | 1 | Phase C Power Scheduling Setting | RW | I16 | kW | 100 | Phase C Power Scheduling Setting |  |  |  |  | energy
1.2.4 | 42 | 50207 | 1 | Battery Power Scheduling Setting | RW | I16 | kW | 100 | [5 empty] | energy
1.2.4 | 43 | 50208 | 1 | Max. AC Power Limit Setting | RW | I16 | kW | 100 | [5 empty] | energy
1.2.4 | 44 | 50209 | 1 | Min. AC Power Limit Setting | RW | I16 | kW | 100 | [5 empty] | energy
1.2.4 | 45 | 50210 | 1 | Priority of Power Output Setting | RW | U16 | NA | 1 | 0: PV Output Priority 1: Battery Output Priority |  | Switch | solinteg-pwr-schdl-prio.map |  | energy
1.2.4 | 46 | 50211 | 1 | PV Power Scheduling Setting | RW | U16 | kW | 100 | [5 empty] | energy
1.2.4 | 47 | 52500 | 1 | Battery Configuration | RW | U16 | N/A | 1 | Please refer to table 3.7 |  |  | solinteg-battery-conf.map |  | batterylevel
1.2.4 | 48 | 52501 | 1 | Battery Protocol configuration | RW | U16 | N/A | 1 |  |  |  | solinteg-battery-proto.js |  | batterylevel
1.2.4 | 49 | 52502 | 1 | On-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | batterylevel
1.2.4 | 50 | 52503 | 1 | On-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%] |  |  |  |  | batterylevel
1.2.4 | 51 | 52504 | 1 | Off-grid SOC Protection | RW | U16 | N/A | 1 | 0: OFF 1: ON |  | Switch |  |  | batterylevel
1.2.4 | 52 | 52505 | 1 | Off-grid Battery End SOC | RW | U16 | N/A | 1000 | [0.0%-100.0%] |  |  |  |  | batterylevel
1.2.4 | 53 | 53006 | 1 | Period Enable Flag | RW | U16 | N/A | 1 | bit0- bit5 stands for period1-period6, bit7-bit15 reserved; 0: disable 1: enable | 1 | Switch |  |  | settings
1.2.4 | 54 | 53007 | 1 | Charge/Discharge Setting | RW | U16 | N/A | 1 | Period1: 0:NONE 1:charge 2:discharge |  |  |  |  | batterylevel
1.2.4 | 55 | 53008 | 1 | Battery Charge By | RW | U16 | N/A | 1 | Period1: 0:PV 1:PV+GRID |  | Switch |  |  | energy
1.2.4 | 56 | 53009 | 1 | reserved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF |  |  |  | 1 | none
1.2.4 | 57 | 53010 | 1 | Power Limit | RW | U16 | % | 1000 | Period1: [0.0-100.0%] |  |  |  |  | energy
1.2.4 | 58 | 53011 | 1 | reserved | RW | U16 | N/A | 1 | Period1: Reserved: 0xFF |  |  |  | 1 | none
1.2.4 | 59 | 53012 | 1 | Start Time | RW | U16 | N/A | 1 | Period1: High 8bits(Hour): [0,23] Low 8bits(Mins): [0,59] | 1 |  |  |  | time
1.2.4 | 60 | 53013 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 61 | 53014 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period2 Note Same as Period1 |  |  |  |  | batterylevel
1.2.4 | 62 | 53015 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  |  | Switch |  |  | energy
1.2.4 | 63 | 53016 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 64 | 53017 | 1 | Power Limit | RW | U16 | N/A | 1000 | [5 empty] | energy
1.2.4 | 65 | 53018 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 66 | 53019 | 1 | Start Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 67 | 53020 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 68 | 53021 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period3 Note Same as Period1 |  |  |  |  | batterylevel
1.2.4 | 69 | 53022 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  |  | Switch |  |  | energy
1.2.4 | 70 | 53023 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 71 | 53024 | 1 | Power Limit | RW | U16 | N/A | 1000 | [5 empty] | energy
1.2.4 | 72 | 53025 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 73 | 53026 | 1 | Start Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 74 | 53027 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 75 | 53028 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period4 Note Same as Period1 |  |  |  |  | batterylevel
1.2.4 | 76 | 53029 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  |  | Switch |  |  | energy
1.2.4 | 77 | 53030 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 78 | 53031 | 1 | Power Limit | RW | U16 | N/A | 1000 | [5 empty] | energy
1.2.4 | 79 | 53032 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 80 | 53033 | 1 | Start Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 81 | 53034 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 82 | 53035 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period5 Note Same as Period1 |  |  |  |  | batterylevel
1.2.4 | 83 | 53036 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  |  | Switch |  |  | energy
1.2.4 | 84 | 53037 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 85 | 53038 | 1 | Power Limit | RW | U16 | N/A | 1000 | [5 empty] | energy
1.2.4 | 86 | 53039 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 87 | 53040 | 1 | Start Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 88 | 53041 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 89 | 53042 | 1 | Charge/Discharge | RW | U16 | N/A | 1 | Period6 Note Same as Period1 |  |  |  |  | batterylevel
1.2.4 | 90 | 53043 | 1 | Battery Charge By | RW | U16 | N/A | 1 |  |  | Switch |  |  | energy
1.2.4 | 91 | 53044 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 92 | 53045 | 1 | Power Limit | RW | U16 | N/A | 1000 | [5 empty] | energy
1.2.4 | 93 | 53046 | 1 | reserved | RW | U16 | N/A | 1 |  |  |  |  | 1 | none
1.2.4 | 94 | 53047 | 1 | Start Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 95 | 53048 | 1 | Stop Time | RW | U16 | N/A | 1 |  | 1 |  |  |  | time
1.2.4 | 96 | 53500 | 8 | BMSVersion | WO | STR | N/A | 1 | Only for BMS access to EMS |  |  |  | 1 | batterylevel
1.2.4 | 97 | 53508 | 1 | BMS Status | WO | U16 | N/A | 1 | Please refer to Table 3.8 Only for BMS access to EMS |  |  |  | 1 | batterylevel
1.2.4 | 98 | 53509 | 2 | BMS ErrorCode | WO | U32 | N/A | 1 | Please refer to Table 3.9 Only for BMS access to EMS |  |  |  | 1 | batterylevel
1.2.4 | 99 | 53511 | 2 | BMS Protection Code | WO | U32 | N/A | 1 |  |  |  |  | 1 | batterylevel
1.2.4 | 100 | 53513 | 2 | BMS WarnCode | WO | U32 | N/A | 1 |  |  |  |  | 1 | batterylevel
1.2.4 | 101 | 53515 | 1 | BMSChargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS |  |  |  | 1 | batterylevel
1.2.4 | 102 | 53516 | 1 | BMSChargeCurrMax | WO | U16 | A | 10 |  |  |  |  | 1 | batterylevel
1.2.4 | 103 | 53517 | 1 | BMSDishargeVoltLimit | WO | U16 | V | 10 | Only for BMS access to EMS |  |  |  | 1 | batterylevel
1.2.4 | 104 | 53518 | 1 | BMSDishargeCurrMax | WO | U16 | A | 10 |  |  |  |  | 1 | batterylevel
1.2.4 | 105 | 53519 | 1 | BMSBatSOC | WO | U16 | % | 100 |  |  |  |  | 1 | batterylevel
1.2.4 | 106 | 53520 | 1 | BMSBatSOH | WO | U16 | % | 100 |  |  |  |  | 1 | batterylevel
1.2.4 | 107 | 53521 | 1 | BMSBatVoltage | WO | U16 | V | 10 |  |  |  |  | 1 | batterylevel
1.2.4 | 108 | 53522 | 1 | BMSBatCurrent | WO | I16 | A | 10 |  |  |  |  | 1 | batterylevel
1.2.4 | 109 | 53523 | 1 | BMSBatTemp | WO | I16 | °C | 10 |  |  |  |  | 1 | batterylevel
1.2.5 | 1 | 50200 | 1 | Off-grid function Switch | WO | U16 | N/A | 1 | 0:OFF 1:ON |  | Switch |  |  | switch
1.2.5 | 2 | 50201 | 1 | Clear Off-grid Over-loading Protection Flag | WO | U16 | N/A | 1 | Write 1 to clear |  | Switch |  |  | switch
Note on M1: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: If not a Number item

## Data Types
Solinteg Data Type | Modbus Binding Data Type
U16 | uint16
U32 | uint32
I16 | int16
I32 | int32
STR | TODO

## Working Mode
| 32768 | 16384 | 8192 | 4096 | 2048 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2 | 1
Bit | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
General Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 257
Economic Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 258
UPS Mode | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 259
Off Grid Mode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512
EMS_ACCtrlMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 769
EMS_GeneralMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 770
EMS_BattCtrlMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 771
EMS_OffGridMode | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 772